## DAR Old (hidden)
| Project No. | Date
| Sheet No. | Computed by
Subject | Checked by | Approved by
DESIGN CALCULATION
SHEET
of

## DAR (hidden)
Design calculation sheet
Project no.: | Date: | Sheet no.: | 25 | 25 | Computed by:
Subject |  |  |  |  | Checked by:
Approved by:
of

## FM200-SI
Design calculation sheet
Project no: | D0271 |  | Date: | 2003-09-03 | Sheet no.: | 1 | 1 | Computed by: | R.G.H
Subject: | Dubai Royal Airwing | [6 empty] | Checked by: | M.A
| Administration Archive - FM200 Total Flooding Quantity | [6 empty] | Approved by:
| Basis : | NFPA 2001, Standard on Clean Agent Fire Extinguishing Systems, 2000 Edition
The amount of Halocarbon agent required to achieve the design concentration shall be calculated from
the following Formula
| Hazard Class | = | Class C
| W | = | Weight of FM200 (kg)
| V | = | Net Volume of the Hazard |  |  | = | 150 | (m3)
| C | = | FM 200 Design Concentration |  |  | = | 9 | %
| sf | = | Safety actor |  |  | = | 1.2
|  |  | Resulting Concentration |  |  | = | 10.8 | %
| t | = | Minimum anticipated temp. |  |  | = | 60 | º C
of the protected volume
| S | = | Specific Volume of superheated |  |  | = | 0.1578 | (m3/kg)
agent vapor at 1 atmosphere and
the temperature t
| W | = | 150 | x [ |  | 10.8 |  | ]
|  |  | 0.1578 |  | 100 | - | 10.8
| W | = | 116 | kg of FM-200 agent
Class A Fires : |  | Fire in ordinary combustible materials, such as wood, cloth, paper, rubber, and many plastics.
Class B Fires : |  | Fire in flammable liquids, oils, greases, tars, oil-base paints, lacquers, and flammable gases.
Class C Fires : |  | Fire that involves energized electrical equipment where the electrical resistivity of the
the extinguishing media is of importance.
3-4 Design Concentration Requirements.
3-4.2.1 The flame extinguishing concentration for Class B fuels shall be determined by the cup burner method
described in Appendix B.
3-4.2.2 The flame extinguishing concentration for Class A fuels shall be determined by test as part of a
listing program. As a minimum, the listing program shall conform to UL 2127, Standard for Inert Gas
Clean Agent Extinguishing System Units, or UL 2166, Standard for Halocarbon Clean Agent Extinguishing
System Units, or equivalent.
3-4.2.3 The minimum design concentration for a Class B fuel hazard or an only manually actuated system
shall be the extinguishing concentration, as determined in 3-4.2.1, times a safety factor of 1.3.
3-4.2.4 The minimum design concentration for a Class A surface fire hazard shall be the extinguishing
concentration as determined in 3-4.2.2, times a safety factor of 1.2.
3-4.2.5 Minimum design concentration for Class C hazards shall be at least that for Class A surface fire.
of

## FM200-Imperial
Design calculation sheet
Project no: | D0271 |  | Date: | 2003-09-03 | Sheet no.: | 1 | 1 | Computed by: | R.G.H
Subject: | Dubai Royal Airwing | [6 empty] | Checked by: | M.A
| Adminidtration Archive - FM200 Total Flooding Quantity | [6 empty] | Approved by:
| Basis : | NFPA 2001, Standard on Clean Agent Fire Extinguishing Systems, 2000 Edition
The amount of Halocarbon agent required to achieve the design concentration shall be calculated from
the following Formula
| Hazard Class | = | Class C
| W | = | Weight of FM200 (lb)
| V | = | Net Volume of the Hazard |  |  | = | 4500 | (ft3)
| C | = | FM 200 Design Concentration |  |  | = | 7 | %
| sf | = | Safety actor |  |  | = | 1.2
|  |  | Resulting Concentration |  |  | = | 8.4 | %
| t | = | Minimum anticipated temp. |  |  | = | 70 | º F
of the protected volume
| S | = | Specific Volume of superheated |  |  | = | 2.2075 | (ft3/lb)
agent vapor at 1 atmosphere and
the temperature t
| W | = | 4500 | x [ |  | 8.4 |  | ]
|  |  | 2.2075 |  | 100 | - | 8.4
| W | = | 187 | lbs of FM-200 agent
Class A Fires : |  | Fire in ordinary combustible materials, such as wood, cloth, paper, rubber, and many plastics.
Class B Fires : |  | Fire in flammable liquids, oils, greases, tars, oil-base paints, lacquers, and flammable gases.
Class C Fires : |  | Fire that involves energized electrical equipment where the electrical resistivity of the
the extinguishing media is of importance.
3-4 Design Concentration Requirements.
3-4.2.1 The flame extinguishing concentration for Class B fuels shall be determined by the cup burner method
described in Appendix B.
3-4.2.2 The flame extinguishing concentration for Class A fuels shall be determined by test as part of a
listing program. As a minimum, the listing program shall conform to UL 2127, Standard for Inert Gas
Clean Agent Extinguishing System Units, or UL 2166, Standard for Halocarbon Clean Agent Extinguishing
System Units, or equivalent.
3-4.2.3 The minimum design concentration for a Class B fuel hazard or an only manually actuated system
shall be the extinguishing concentration, as determined in 3-4.2.1, times a safety factor of 1.3.
3-4.2.4 The minimum design concentration for a Class A surface fire hazard shall be the extinguishing
concentration as determined in 3-4.2.2, times a safety factor of 1.2.
3-4.2.5 Minimum design concentration for Class C hazards shall be at least that for Class A surface fire.
of

## Cylinder Sizes
Design calculation sheet
Project no: | D0271 | Date: | 2003-09-03 | Sheet no.: | 1 1 | Computed by: | R.G.H
Subject: | Royal Airwing |  |  |  |  | Checked by: | M.A
| Cylinder Sizes for CHEMETRON |  |  |  |  | Approved by:
Design calculation sheet
Project no: | D0271 | Date: | 2003-09-03 | Sheet no.: | 1 1 | Computed by: | R.G.H
Subject: | Royal Airwing |  |  |  |  | Checked by: | M.A
| Cylinder Sizes for CHEMETRON |  |  |  |  | Approved by:
of
of

## Data
Design calculation sheet
Project no: | D0271 | Date: | 2003-09-03 | Sheet no.: | 1 1 | Computed by: | R.G.H
Subject: | Dubai Royal Airwing |  |  |  |  | Checked by: | M.A
| FM200 Total Flooding Quantity |  |  |  |  | Approved by:
| Basis : | NFPA 2001, Standard on Clean Agent Fire Extinguishing Systems, 2000 Edition
| Temperature | Specific Vapor |  | Temperature | Specific Vapor
| t | Volume |  | t | Volume
| ºF | (ft3/lb) |  | ºC | (m3/kg)
| 10 | 1.9264 |  | -10 | 0.1215
| 20 | 1.9736 |  | -5 | 0.1241
| 30 | 2.021 |  | 0 | 0.1268
| 40 | 2.0678 |  | 5 | 0.1294
| 50 | 2.1146 |  | 10 | 0.132
| 60 | 2.1612 |  | 15 | 0.1347
| 70 | 2.2075 |  | 20 | 0.1373
| 80 | 2.2538 |  | 25 | 0.1399
| 90 | 2.2994 |  | 30 | 0.1425
| 100 | 2.3452 |  | 35 | 0.145
| 110 | 2.3912 |  | 40 | 0.1476
| 120 | 2.4366 |  | 45 | 0.1502
| 130 | 2.482 |  | 50 | 0.1527
| 140 | 2.5272 |  | 55 | 0.1553
| 150 | 2.5727 |  | 60 | 0.1578
| 160 | 2.6171 |  | 65 | 0.1604
| 170 | 2.6624 |  | 70 | 0.1629
| 180 | 2.7071 |  | 75 | 0.1654
| 190 | 2.7518 |  | 80 | 0.1679
| 200 | 2.7954 |  | 85 | 0.1704
| from Table A-3-5.1 (k) |  |  | 90 | 0.173
from Table A-3-5.1 (l)
Design
Conctentration
% per Volume
6
7
8
9
10
11
12
13
14
15
of

## Cup Burner Extinguishing Value
Design calculation sheet
Project no: | D0271 | Date: | 2003-09-03 | Sheet no.: | 1 1 | Computed by: | R.G.H
Subject: | Royal Airwing |  |  |  |  | Checked by: | M.A
| FM200 Total Flooding Quantity |  |  |  |  | Approved by:
Cup burner extinguishing values are defined by ISO Standard 14520
The following has been extracted fro an article published on the internet
http://www.firetrace.com/99hotwccuppost.html
DEVELOPMENT OF A STANDARD CUP BURNER APPARATUS: NFPA AND ISO STANDARD
METHODS
The cup burner apparatus, originally developed by Hirst and Booth in the late 1970s has been widely employed
in laboratory-scale fire suppression testing of the recently developed clean extinguishing agents. The wide
variation in extinguishing concentrations obtained via the cup burner method, due to variations in apparatus
design and/or operation, has resulted in a call for standardization of the cup burner method by the ISO 14520
Committee on Gaseous Fire Extinguishing Systems and by the NFPA 2001 Technical Committee.
EXTINGUISHING VALUES FOR HALOCARBONS: HFC-227ea
Extinguishing concentrations of FM-200Ò (HFC-227ea) were determined for six liquid fuels employing the
standard apparatus and procedures described in the current drafts of NFPA 2001 Standard on Clean Agent
Fire Extinguishing Systems and ISO 14520 Gaseous Fire-Extinguishing Systems. The extinguishing values
and statistical analysis of the data are summarized in Tables 1 through 6.
Extract from Table 1. HFC-227ea Extinguishing Concentrations for Ethyl Alcohol, denatured | [6 empty] | 8.5%
Extract from Table 2. HFC-227eaExtinguishing Concentrations for Toluene | [6 empty] | 5%
Extract from Table 3. HFC-227ea Extinguishing Concentrations for n-Heptane | [6 empty] | 6.5%
Extract from Table 4. HFC-227ea Extinguishing Concentrations for Acetone | [6 empty] | 6.8%
Extract from Table 5. HFC-227ea Extinguishing Concentrations for 2-Propanol | [6 empty] | 7.2%
Extract from Table 6. Extinguishing Concentrations for Methyl Alcohol | [6 empty] | 10.2%
of

## Personal Notes
Design calculation sheet
Project no: | D0271 | Date: | 2003-09-03 | Sheet no.: | 1 1 | Computed by: | R.G.H
Subject: | Royal Airwing |  |  |  |  | Checked by: | M.A
| FM200 Total Flooding Quantity |  |  |  |  | Approved by:
of

## About FM200 Calculator
FM200 Calculator
Version 1.0
Released 5-09-03
R.G.H