## Sheet1
Stair Pressurization Estimator
Disclaimer: This calculator is for estimating purposes only and is not for final design calculations. This does not take the place of a rational analysis and does not incorporate all factors that could impact stair pressurization. Consult a licensed fire protection engineer.
Description |  | Value | Unit
Building Inputs
Number of Stories |  | 13 | Stories
Average Floor Height |  | 12 | Feet
Average Building Perimeter per Floor |  | 264 | Feet
Number of Stairways |  | 2 | Stairs
Stair Length |  | 19 | Feet
Stair Width |  | 8.7 | Feet
Total Length of Stair Wall Bordering Inside |  | 27.7 | Feet
Total Length of Stair Wall Bordering Outside |  | 27.7 | Feet
Stair Door Width |  | 3 | Feet
Stair Door Height |  | 7 | Feet
Number of Doors Between Stair and Building |  | 26 | Doors
Number of Doors Between Stair and Outside |  | 1 | Doors
Model Inputs
Max Pressure Difference |  | 0.35 | in. H20
Min Pressure Difference |  | 0.1 | in. H20
Construction |  | Average | -
Outdoor Design Temp - Summer |  | 96 | F
Outdoor Design Temp - Winter |  | 10 | F
Summary
Required Flow Rate - Summer |  | 5540.3972 | CFM
Required Flow Rate - Winter |  | 4961.5322 | CFM
Assumptions: All equations, calculations from Handbook of Smoke Control Engineering, 2nd Edition, Klote All stairs are uniform in dimension All stair doors closed Building/stair temperature is 70F Atmospheric pressure is 14.7 psi
Parameter | Abbreviation | Value | Unit
Area Between Stair and Building | ASB | 4.6353 | SF
Area Between Building and Outside | ABO | 2.1875 | SF
Area Between Stair and Outside | ASOu | 0.47533 | SF
Area Between Stair and Roof | ASOr | 0.0085956 | SF
Winter
Outdoor Air Density | ρo | 0.084436 | lb./ft3
Temperature Factor | FT | 0.0017057 | in. H2O/ft
Flow Area Factor | FR | 5.4904 | -
Pressure Difference between Stair and Building, top | PSBt | 0.14846 | in. H2O
Pressure Difference between Stair and Building, bottom | PSBb | 0.1 | in. H2O
Pressure Difference between Stair and Building, average | PSBav | 0.12423 | in. H2O
Pressure Difference between Stair and Outside, bottom | PSOb | 0.54904 | in. H2O
Pressure Difference between Stair and Outside, top | PSOt | 0.81513 | in. H2O
Pressure Difference between Stair and Outside, average | PSOav | 0.68208 | in. H2O
Mass Flow Rate between Stair and Building | mSB | 5.2992 | lb/s
Mass Flow Rate between Stair and Outside, wall leaks | mSOu | 1.2733 | lb/s
Mass Flow Rate between Stair and Outside, door | mSOd | 0.38453 | lb/s
Mass Flow Rate between Stair and Outside, roof | mSOr | 0.025171 | lb/s
Total Mass Flow Rate | m | 6.9822 | lb/s
Total Volumetric Flow Rate | V | 4961.5322 | CFM
Summer
Outdoor Air Density | ρo | 0.071376 | lb./ft3
Temperature Factor | FT | -0.00062481 | in. H2O/ft
Flow Area Factor | FR | 5.4904 | -
Pressure Difference between Stair and Building, top | PSBt | 0.1 | in. H2O
Pressure Difference between Stair and Building, bottom | PSBb | 0.11775 | in. H2O
Pressure Difference between Stair and Building, average | PSBav | 0.10888 | in. H2O
Pressure Difference between Stair and Outside, bottom | PSOb | 0.64651 | in. H2O
Pressure Difference between Stair and Outside, top | PSOt | 0.54904 | in. H2O
Pressure Difference between Stair and Outside, average | PSOav | 0.59777 | in. H2O
Mass Flow Rate between Stair and Building | mSB | 4.9609 | lb/s
Mass Flow Rate between Stair and Outside, wall leaks | mSOu | 1.192 | lb/s
Mass Flow Rate between Stair and Outside, door | mSOd | 0.41727 | lb/s
Mass Flow Rate between Stair and Outside, roof | mSOr | 0.020658 | lb/s
Total Mass Flow Rate | m | 6.5909 | lb/s
Total Volumetric Flow Rate | V | 5540.3972 | CFM
Stairwell Temp | 70 | F
Building Temp | 70 | F
Atmospheric Pressure | 14.7 | psi
Stair Area | 165.3 | SF
Total Height | 156 | Feet
Stair Perimeter | 55.4 | Feet
Door Area | 21 | SF
Leakage Area Stair Walls | 0.00011
Loose | 0.00035
Average | 0.00011
Tight | 1.4e-05
Leakage Area Stair Floor | 5.2e-05
Loose | 0.00017
Average | 5.2e-05
Tight | 6.6e-06
Leakage Area Doors Closed | 0.16
Loose | 0.24
Average | 0.16
Tight | 0.08